{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":76,"n_cols":9,"rows_kept":76,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ABQ-C"]
[]
[]
[]
[]
["","","","","","ABQ71CV1","ABQ100CV1","ABQ125CV1","ABQ140CV1"]
["Accessoires standard","Manuel d'installation","","","","Manuel d'installation"]
["","Manuel d’utilisation","","","","Manuel d’utilisation"]
["","Vis+Rondelle","","","","Vis+Rondelle"]
["","Télécommande infrarouge","","","","Télécommande infrarouge"]
["","Grille de verrouillage de protection","","","","Grille de verrouillage de protection"]
["","Batterie","","","","Batterie"]
["Raccords de tuyauterie","Liquide","","DE","mm","9.52"]
["","Gaz","","DE","mm","15.88"]
["","Drain","","","","19.05"]
["Puissance absorbée","Rafraîchissement","","Nom.","kW","0.128"]
["","Chauffage","","Nom.","kW","0.128"]
["Sound power level","Rafraîchissement","","","dBA","64"]
["","Chauffage","","","dBA","64"]
["Dimensions","Unité","","Largeur","mm","600"]
["","","","Profondeur","mm","1,007"]
["","","","Hauteur","mm","285"]
["Caisson","Matériau","","","","Acier galvanisé"]
["Poids","Unité","","","kg","35"]
["Ventilateur","Pression statique externe","","Haute","Pa","90"]
["","","","Nom.","Pa","77"]
["","","","Basse","Pa","64"]
["Power supply","Phase","","","","1~"]
["","Fréquence","","","Hz","50"]
["","Nom","","","","V1"]
["","Tension","","","V","220-240"]
["Puissance absorbée","Chauffage","","Nom.","kW","","0.109"]
["","Rafraîchissement","","Nom.","kW","","0.109"]
["Ventilateur","Pression statique externe","","Haute","Pa","","70","150","150"]
["","","","Basse","Pa","","45","111","92"]
["Caisson","Matériau","","","","","Acier galvanisé"]
["Dimensions","Unité","","Hauteur","mm","","378","378","378"]
["","","","Largeur","mm","","541","1300","1500"]
["","","","Profondeur","mm","","1045","541","541"]
["Poids","Unité","","","kg","","44","50","56"]
["Ventilateur","Débit d'air","Rafraîchissement","Haut","m³/min","","22.7","40.5","48.7"]
["","","","Nom.","m³/min","","20.5","37","44"]
["","","","Bas","m³/min","","18.3","34.8","37.9"]
["","","Chauffage","Haut","m³/min","","22.7","40.5","48.7"]
["","","","Nom.","m³/min","","20.5","37.4","43.9"]
["","","","Bas","m³/min","","18.3","34.8","37.9"]
["","Pression statique externe","","Nom.","Pa","","57","128","122"]
["Niveau de puissance sonore","Rafraîchissement","","","dBA","","60","72","73"]
["","Chauffage","","","dBA","","60","72","73"]
["Niveau de pression sonore","Rafraîchissement","","Haut","dBA","","41","53","55"]
["","","","Nom.","dBA","","38"]
["","","","Bas","dBA","","36","50","50"]
["","Chauffage","","Haut","dBA","","41","53","55"]
["","","","Nom.","dBA","","38"]
["","","","Bas","dBA","","36","50","50"]
["Raccords de tuyauterie","Liquide","","DE","mm","","9.52","9.52","9.52"]
["","Gaz","","DE","mm","","15.88","15.9","15.9"]
["","Évacuation","","","","","19.05"]
["Accessoires standard","Installation manual","","","","","Installation manual"]
["","Wireless remote control","","","","","Wireless remote control"]
["","Cover lock grill","","","","","Cover lock grill"]
["","Battery","","","","","Battery"]
["","Screw+Washer","","","","","Screw+Washer"]
["","Operation manual","","","","","Operation manual"]
["Alimentation électrique","Nom","","","","","V1"]
["","Phase","","","","","1~"]
["","Fréquence","","","Hz","","50"]
["","Tension","","","V","","220-240"]
["Puissance frigorifique","Puissance totale","","Nom.","kW","","","12.10","13.00"]
["Puissance calorifique","Puissance totale","","Nom.","kW","","","13.5","15.5"]
["Caisson","Couleur","","","","","","Tôle d'acier galvanisé / Non peinte","Tôle d'acier galvanisé / Non peinte"]
["Ventil.","Débit d'air","Refroidissement","Moyen","m³/min","","","37","44"]
["","","Chauffage","Moyen","m³/min","","","37.4","43.9"]
["Niveau de pression sonore","Refroidissement","","Moyen","dBA","","","52","53"]
["","Chauffage","","Moyen","dBA","","","52","53"]
["Systèmes de commande","Télécommande infrarouge","","","","","","ARCWLA","ARCWLA"]