{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":8,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DW1P-H"]
[]
[]
[]
[]
["","","","","","EWAA011DAW1P-H-","EWAA014DAW1P-H-","EWAA016DAW1P-H-"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","47.7","50.8","51.0"]
["Composants hydrauliques","Vase d'expansion","","Volume","L","8","8","8"]
["Plage de fonctionnement","Côté air","Rafraîchissement","Min.","°CBS","10","10","10"]
["","","","Max.","°CBS","43","43","43"]
["","Côté eau","Rafraîchissement","Max.","°CBS","22","22","22"]
["","","","Min.","°CBS","5","5","5"]
["Charge de réfrigérant","Par circuit","","","kg","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6"]
["Compresseur","Type","","","","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter"]
["","Méthode de démarrage","","","","Commandé par Inverter","Commandé par Inverter","Commandé par Inverter"]
["","Quantité_","","","","1","1","1"]
["Échangeur de chaleur air","Type","","","","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral"]
["Poids","Unité","","","kg","147","147","147"]
["EER","","","","","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Réfrigérant","PRP","","","","675.0","675.0","675.0"]
["","Type","","","","R-32","R-32","R-32"]
["","Circuits","","Quantité","","1","1","1"]
["","Commande","","","","Détendeur électronique","Détendeur électronique","Détendeur électronique"]
["Moteur de ventil.","Vitesse","Rafraîchissement","Nom.","tr/min","550","650","650"]
["Puissance frigorifique","Nom.","","","kW","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Échangeur de chaleur - eau","Volume d'eau","","","L","2","2","2"]
["","Volume min. d'eau dans le système","","","L","20 (6)","20 (6)","20 (6)"]
["","Type","","","","Échangeur de chaleur à plaques","Échangeur de chaleur à plaques","Échangeur de chaleur à plaques"]
["Power input","Rafraîchissement","","Nom.","kW","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["Sound power level","Rafraîchissement","","Nom.","dBA","67.0","69.0","69.0"]
["Dimensions","Unité","","Largeur","mm","1,380","1,380","1,380"]
["","","","Profondeur","mm","460","460","460"]
["","","","Hauteur","mm","870","870","870"]
["Commande de puissance","Méthode","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Ventilateur","Débit d'air","Rafraîchissement","Nom.","m³/min","70","85","85"]
["Compresseur","Méthode de démarrage","","","","Commande","Commande","Commande"]
["Power supply","Phase","","","","3~","3~","3~"]
["","Fréquence","","","Hz","50","50","50"]
["","Nom","","","","W1","W1","W1"]
["","Tension","","","V","400","400","400"]
["Remarques","","","","","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS"]
["","","","","","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS"]
["","","","","","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Conformément à la norme EN14825","(5) - Conformément à la norme EN14825","(5) - Conformément à la norme EN14825"]
["","","","","","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation."]
["","","","","","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement."]