{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":73,"n_cols":11,"rows_kept":73,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-L"]
[]
[]
[]
[]
["","","","","","RXS20L2V1B","RXS25L2V1B","RXS35L2V1B","RXS42L2V1B","RXS50L2V1B","RXS60L2V1B"]
["Niveau de pression sonore","Chauffage","","Haut","dBA","47","47","48","48"]
["","Rafraîchissement","","Haut","dBA","46","46","48","48"]
["Accessoires standard","Bouchon d’évacuation","","","","1","1","","1"]
["","Manuel d'installation","","","","1","1","1","1"]
["","Étiquette de charge de réfrigérant","","","","1","1","1"]
["","Étiquettes multilingues de gaz à effet de serre fluorés","","","","1","1","Étiquettes multilingues de gaz à effet de serre fluorés"]
["Réfrigérant","Charge","","","TCO2Eq","2.1","2.1","2.5","2.7"]
["","PRP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","1.0","1.0","1.20","1.3"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A"]
["Moteur de ventilateur","Vitesse","Rafraîchissement","Extra lent","tr/min","780","780","780","790"]
["","","Chauffage","Extra lent","tr/min","740","740","740","780"]
["Plage de fonctionnement","Rafraîchissement","Temp. ambiante","Max.","°CBS","46","46","46","46"]
["","","","Min.","°CBS","-10","-10","-10","-10"]
["","Chauffage","Ambiante","Max.","°CBH","18","18","18","18"]
["","","","Min.","°CBH","-15","-15","-15","-15"]
["Raccords de tuyauterie","Dénivelé","UI - UE","Max.","m","","","15"]
["","Charge de réfrigérant supplémentaire","","","kg/m","","","0,020 (pour longueur de tuyauterie supérieure à 10 m)"]
["Dimensions","Unité","","Largeur","mm","765","765","765","765"]
["","","","Profondeur","mm","285","285","285","285"]
["","","","Hauteur","mm","550","550","550","550"]
["Compresseur","Type","","","","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique"]
["Poids","Unité","","","kg","34","34","34","39"]
["Ventilateur","Débit d'air","Chauffage","Extra lent","cfm","904","904","904","960"]
["","","","Extra lent","m³/min","25.6","25.6","25.6","27.2"]
["","","Rafraîchissement","Extra lent","m³/min","30.1","30.1","30.1","30.6"]
["","","","Extra lent","cfm","1,063","1,063","1,063","1,080"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50","50"]
["","Tension","","","V","220-240","220-240","220-240","220-240"]
["Remarques","","","","","(1) - 220V","(1) - 220V","(1) - 220V","(1) - 220V","(1) - 220V"]
["","","","","","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V"]
["","","","","","(3) - 240V","(3) - 240V","(3) - 240V","(3) - 240V","(3) - 240V"]
["","","","","","(4) - Contient des gaz à effet de serre fluorés.","(4) - Contient des gaz à effet de serre fluorés.","(4) - Contient des gaz à effet de serre fluorés.","(4) - Contient des gaz à effet de serre fluorés."]
["Accessoires standard","Bouchon d'évacuation","","","","","","1"]
["Ventilateur","Débit d’air","Rafraîchissement","Extra lent","m³/min","","","","","48.9","45.0"]
["","","Chauffage","Extra lent","m³/min","","","","","43.1","46.3"]
["","","","Extra lent","cfm","","","","","1727","1589"]
["","","Chauffage","Extra lent","cfm","","","","","1522","1635"]
["Dimensions","Unité","","Hauteur","mm","","","","","735","735"]
["","","","Largeur","mm","","","","","825","825"]
["","","","Profondeur","mm","","","","","300","300"]
["Poids","Unité","","","kg","","","","","47","48"]
["Moteur de ventilateur","Vitesse","Rafraîchissement","Extra lent","tr/min","","","","","670"]
["","","Chauffage","Extra lent","tr/min","","","","","670"]
["Compresseur","Type","","","","","","","","Compresseur swing hermétique","Compresseur swing hermétique"]
["Plage de fonctionnement","Rafraîchissement","Temp. ambiante","Min.","°CBS","","","","","-10","-10"]
["","","","Max.","°CBS","","","","","46","46"]
["","Chauffage","Temp. ambiante","Min.","°CBH","","","","","-15","-15"]
["","","","Max.","°CBH","","","","","18","18"]
["Niveau de pression sonore","Rafraîchissement","","Haut","dBA","","","","","48","49"]
["","","","Bas","dBA","","","","","44","46"]
["","Chauffage","","Haut","dBA","","","","","48","49"]
["","","","Bas","dBA","","","","","45","46"]
["Réfrigérant","Type","","","","","","","","R-410A","R-410A"]
["","Charge","","","kg","","","","","1.7","1.5"]
["","Charge","","","tCO2Eq","","","","","3.5","3.1"]
["","PRP","","","","","","","","2087.5","2087.5"]
["Raccords de tuyauterie","Longueur de tuyauterie","Max.","UE - UI","m","","","","","30","30"]
["","Charge de réfrigérant supplémentaire","","","kg/m","","","","","0,020 (pour longueur de tuyauterie supérieure à 10 m)","0,020 (pour longueur de tuyauterie supérieure à 10 m)"]
["","Dénivelé","UI - UE","Max.","m","","","","","20.0","20"]
["Accessoires standard","Installation manual","","","","","","","","1","1"]
["","Drain plug","","","","","","","","1","1"]
["Alimentation électrique","Phase","","","","","","","","1~","1~"]
["","Fréquence","","","Hz","","","","","50","50"]
["","Tension","","","V","","","","","220-230-240","220-230-240"]
["Remarques","","","","","","","","","","(1) - 230 V"]