{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Geluidsdrukniveau","Koelen","","Nom.","dBA","79","79","79","79","79","79","79"]
["Bedrijfsbereik","Waterkant","Verdamper","Min.","°CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Max.","°CDB","25","25","25","25","25","25","25"]
["Compressor","Type","","","","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor"]
["","Starting method","","","","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster"]
["","Hoeveelheid_","","","","1","1","1","1","1","1","1"]
["Gewicht","Bedrijfsgewicht","","","kg","1,211","1,276","1,378","1,415","1,473","1,663","1,607"]
["","Unit","","","kg","1,177","1,233","1,334","1,366","1,416","1,600","1,675"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["Koelmiddel","Type","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","7","7","7","7","7","7","7"]
["","Circuits","","Hoeveelheid","","1","1","1","1","1","1","1"]
["","Vulling","","","kg","18","35","34","37","37","38","38"]
["Koelcapaciteit","Nom.","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.6"]
["Leidingaansluitingen","Waterinlaat/uitlaat verdamper (UD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Opgenomen vermogen","Koelen","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["Geluidsvermogenniveau","Koelen","","Nom.","dBA","89","89","89","89","89","89","89"]
["Afmetingen","Unit","","Breedte","mm","913","913","913","913","913","913","913"]
["","","","Diepte","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Hoogte","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020"]
["Capaciteitsregeling","Minimum koelcapaciteit","","","%","25","25","25","25","25","25","25"]
["","Methode","","","","Traploos","Traploos","Traploos","Traploos","Traploos","Traploos","Traploos"]
["Behuizing","Materiaal","","","","Gegalvaniseerd staal","Gegalvaniseerd staal","Gegalvaniseerd staal","Gegalvaniseerd staal","Gegalvaniseerd staal","Gegalvaniseerd staal","Gegalvaniseerd staal"]
["","Colour","","","","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit"]
["Waterwarmtewisselaar- verdamper","Type","","","","Platenwarmtewisselaar.","Platenwarmtewisselaar.","Platenwarmtewisselaar.","Platenwarmtewisselaar.","Platenwarmtewisselaar.","Platenwarmtewisselaar.","Platenwarmtewisselaar."]
["","Waterdrukdaling","Koeling","Nom.","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["","Watervolume","","","l","14","18","14","17","20","26","26"]
["Power supply","Fase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Spanningsbereik","","Max.","%","10","10","10","10","10","10","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","Frequentie","","","Hz","50","50","50","50","50","50","50"]
["","Spanning","","","V","400","400","400","400","400","400","400"]
["Unit","Max. unitstroom voor de maat van de bedradingen","","","A","83","100","112","127","159","176","198"]
["","Aanloopstroom","","Max.","A","153","153","197","197","197","290","290"]
["","Bedrijfsstroom","Koelen","Nom.","A","39","44","55","60","65","76","84"]
["","","","Max.","A","75","90","100","114","143","158","178"]
["Opmerkingen","","","","","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB"]
["","","","","","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB"]
["","","","","","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825"]
["","","","","","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding"]
["","","","","","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie"]