{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":12,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-J-SS"]
[]
[]
[]
[]
["","","","","","EWWS120J-SS","EWWS140J-SS","EWWS150J-SS","EWWS180J-SS","EWWS210J-SS","EWWS240J-SS","EWWS270J-SS"]
["Koelcapaciteit","Nom.","","","kW","115.2","136.3","154.7","180.6","207.3","241","272.2"]
["Capaciteitsregeling","Methode","","","","Traploos","Traploos","Traploos","Traploos","Traploos","Traploos","Traploos"]
["","Minimum koelcapaciteit","","","%","25","25","25","25","25","25","25"]
["Opgenomen vermogen","Koelen","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Afmetingen","Unit","","Diepte","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Hoogte","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Breedte","mm","913","913","913","913","913","913","913"]
["Gewicht","Bedrijfsgewicht","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Unit","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Behuizing","Kleur","","","","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit","Ivoorwit"]
["","Materiaal","","","","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad","Gegalvaniseerde en geschilderde staalblad"]
["Waterwarmtewisselaar- verdamper","Type","","","","Platenwarmtewisselaar","Platenwarmtewisselaar","Platenwarmtewisselaar","Platenwarmtewisselaar","Platenwarmtewisselaar","Platenwarmtewisselaar","Platenwarmtewisselaar"]
["","Watervolume","","","l","14","18","14","17","20","26","26"]
["Water-warmtewisselaar: verdamper","Waterdrukdaling","Koeling","Nom.","kPa","17.1","16.8","32.8","33.4","31.8","27.9","34.8"]
["Compressor","Hoeveelheid","","","","1","1","1","1","1","1","1"]
["","Type","","","","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor","Monoschroefcompressor"]
["","Aanloopmethode_","","","","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster","Driehoek-ster"]
["Bedrijfsbereik","Waterkant","Verdamper","Min.","°C DB","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°C DB","15","15","15","15","15","15","15"]
["Geluidsvermogenniveau","Koelen","","Nom.","dBA","95","95","95","95","95","95","95"]
["Geluidsdrukniveau","Koelen","","Nom.","dBA","79","79","79","79","79","79","79"]
["Koelmiddel","Type","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","629.5","629.5","629.5","629.5","629.5","629.5","629.5"]
["","Vulling","","","kg","18","35","34","37","37","38","38"]
["Koudemiddel","Circuits","","Aantal","","1","1","1","1","1","1","1"]
["Leidingaansluitingen","Waterinlaat/uitlaat verdamper (UD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Bereik van het energierendement","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Voeding","Fase","","","","3~","3~","3~","3~","3~","3~","3~"]
["Spanningsvoeding","Frequentie","","","Hz","50","50","50","50","50","50","50"]
["","Spanning","","","V","400","400","400","400","400","400","400"]
["","Spanningsbereik","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Spanningsvoeding-=-Spanningsbereik-=-Max.-=-%","%","10","10","10","10","10","10","10"]
["Unit","Aanloopstroom","","Max.","A","154","154","198","198","198","291","291"]
["","Bedrijfsstroom","Koelen","Nom.","A","50","60","70","78","87","105","117"]
["","","","Max.","A","81","96","108","122","141","164","185"]
["","Max. unitstroom voor de maat van de bedradingen","","","A","89","107","120","136","158","183","207"]
["Opmerkingen","","","","","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB","(1) - Koelen: EW 12℃; LW 7℃; omgevingsomstandigheden: 35°CDB"]
["","","","","","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB","(2) - Koelen: EW 23°C; LW 18°C; omgevingsomstandigheden: 35°CDB"]
["","","","","","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Voorwaarde: Ta DB/NB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)","(4) - Voorwaarde: Ta DB/WB 7 °C / 6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825","(5) - Overeenkomstig EN14825"]
["","","","","","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding","(6) - Afhankelijk van de bedrijfsmodus, zie installatiehandleiding"]
["","","","","","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie","(7) - Raadpleeg de werkbereik-tekening voor meer informatie"]