{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":40,"n_cols":6,"rows_kept":40,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VAM-FC9"]
[]
[]
[]
[]
["","","","","","VAM250FCVE9"]
["Opgenomen vermogen - 50Hz","Warmtewisselingsmodus","Nom.","Ultrahoog","kW","0.161"]
["","Bypass-modus","Nom.","Ultrahoog","kW","0.161"]
["Behuizing","Materiaal","","","","Gegalvaniseerde staalplaat"]
["Afmetingen","Unit","","Hoogte","mm","285"]
["","","","Breedte","mm","776"]
["","","","Diepte","mm","525"]
["Gewicht","Unit","","","kg","23"]
["Ventilator","Luchtdebiet - 50Hz","Warmtewisselingsmodus","Ultrahoog","m³/u","250"]
["","","Bypass-modus","Ultrahoog","m³/u","250"]
["","Externe statische druk - 50Hz","","Ultrahoog","Pa","70.0"]
["Werkbereik","Min.","","","°C DB","-15"]
["","Max.","","","°C DB","50"]
["","Relatieve vochtigheid","","","%","80 or less"]
["Geluidsdrukniveau - 50Hz","Warmtewisselingsmodus","","Ultrahoog","dBA","28.0"]
["","Bypass-modus","","Ultrahoog","dBA","28.0"]
["Warmtewisselingssysteem","","","","","Totale warmtewisselaar met lucht-luchtventilatie (voelbare + latente warmte) van het dwarsstroomtype"]
["Warmtewisselingselement","","","","","Speciaal bewerkt onontvlambaar papier"]
["Aansluiting kanaaldiameter","mm","","","","150"]
["Bedrijfsmodus","","","","","Warmtewisselingsmodus, bypass-modus, opfrismodus"]
["SEC-Klasse","","","","","B, Zie opmerking 4"]
["Maximaal debiet bij een externe statische druk van 100 Pa","Debiet","","","m³/u","207"]
["Geluidsvermogenniveau (Lwa)","dB","","","","43"]
["Jaarlijks elektriciteitsverbruik","kWu/a","","","","580"]
["Jaarlijkse besparing op verwarming","Gematigd klimaat","","","kWu/a","4307"]
["","Koud klimaat","","","kWu/a","8426"]
["","Warm klimaat","","","kWu/a","1948"]
["Voeding","Naam","","","","VE"]
["","Fase","","","","1~"]
["Spanningsvoeding","Frequentie","","","Hz","50/60"]
["","Spanning","","","V","220-240/220"]
["Opmerkingen","","","","","(1) - Gemeten volgens JIS B 8628"]
["","","","","","(2) - Gemeten bij referentiedebiet volgens EN13141-7"]
["","","","","","(3) - Conform Gedelegeerde Verordening (EU) nr. 1254/2014"]
["","","","","","(4) - Bij referentiedebiet conform Gedelegeerde Verordening (EU) nr. 1254/2014"]